## System Sizing Worksheet
Electric Load Estimation
1 | Determine electricity consumption in kWh per day. | [7 empty] | ver 1.0.1 - 05/06/06
ENTER HISTORICAL ELECTRICAL CONSUMPTION
| Annual Usage (kWh) |  | 7000 | kWh / year |  |  |  | Enter Data Into Yellow Shaded Cells
| Monthly Usage(kWh) | [6 empty] | Green Cells are Write Protected
| Jan (2009) |  | 797
| Feb (2009) |  | 698
| Mar (2009) |  | 688 |  |  | 50% | % of power to be generated from PV system
| Apr (2009) |  | 602
| May (2009) |  | 478 |  |  | 19.2 | Kilowatt-hrs/day |  | x | 50% | of prower from PV
| Jun (2009) |  | 487
| Jul (2009) |  | 473 |  |  |  | Yearly Consumption |  |  | 7000 | kWh / year
| Aug (2009) |  | 481 |  |  |  | Avg Monthly |  |  | 583.3 | kWh / month
| Sep (2009) |  | 488 |  |  |  | Avg Daily |  |  | 19.2 | kWh / day
| Oct (2009) |  | 515
| Nov (2008) |  | 477
| Dec (2008) |  | 713 |  |  |  | = | 9.6 | (kWh) | PV System Kilowatt-hrs/day
| Ttl Yearly |  | 6897
Array Sizing
2 | Determine average sun hours per day. |  |  |  |  | 5.5 |  | sun-hours/day | Redbook Web Site
3 | Calculate initial PV array size assuming 100% efficiency.
|  | 9.6 | PV System Kilowatt-hrs/day |  |  |  | ÷ | 5.5 | average peak sun hours/day
[7 empty] | = | 1.7 | PV System Design Capacity (kW)
4 | Calculate system inefficiencies / derating factor.
| Derating Factors |  |  |  | Input Values |  |  | Typ. Range
| PV module nameplate DC rating |  |  |  |  | 0.9 |  | .80 - 1.05
| Tilt Factor / Orientation Adjusatment |  |  |  |  | 1 |  | .50 - 1.00 |  | On-line Derating Calculator
| Inverter |  |  |  |  | 0.94 |  | .88 - .96
| Mismatch |  |  |  |  | 0.98 |  | .97 - .995 |  | Derating help page
| Diodes and connections |  |  |  |  | 0.995 |  | .99 - .997
| DC wiring |  |  |  |  | 0.98 |  | .97-.99
| AC wiring |  |  |  |  | 0.99 |  | .98 - .993
| Soiling |  |  |  |  | 0.9 |  | .30 - .995
| System availabilty |  |  |  |  | 0.98 |  | 0.995
| Shading |  |  |  |  | 0.85 |  | 1
| Sun-tracking |  |  |  |  | 1 |  | .95 - 1.00
| Age |  |  |  |  | 0.95 |  | .70 - 1.00
| Overall DC to AC derate factor |  |  |  |  | 0.57 |  | .60 - .75
5 | Calculate array sizing factoring in derating factor. | [6 empty] | 1.7 | PV System Design Capacity (kW)
[7 empty] | ÷ | 0.57 | Derating Factor
[7 empty] | = | 2.9825 | PV Array Installed Kilowatts (DC)
6 | Choose a PV Module
| Make: | Mitsubishi Electronics |  |  |  | Model: | PV-MF165B3
|  | STC rating (w): | 165 |  |  |  |  | CEC rating (w): | 146.9
7 | Determine Number of PV Modules: | [6 empty] | 2982 | PV Array Installed Watts (DC) |  |  |  | Efficency: 13.4%
[7 empty] | ÷ | 146.9 | CEC Rating (w) |  |  |  | Weight: 37 lb (17 Kg)
[7 empty] | = | 21 | Number of Modules |  |  |  | Size:65.3 in. x 32.8 in. x 1.8 in.
[6 empty] | Upgrade |  | We will use 22 Modules to add power and even distribution. |  |  |  |  | Cost: $1020 retail, $558 bargan
[8 empty] | 3124 | Watts ratting |  |  |  | Solar Panel Cost |  | 12276
[13 empty] | sf | Panels | Area
8 | Determine CEC Inverter: | [11 empty] | 14.8739 | sf | 312.3517
[13 empty] | 1.3828 | m2 | 29.0382
| Sharp Corporation | JH-3500U | Utility Interactive Inverter 240Vac L-L, 3.5kW |  | 3185 | 3500 | 91 | Yes | 2005-08-10 |  |  | Votage Max 24.4 |  | per panel
Note on C28: Calculated Value. Protected cell.
Note on D6: Enter best guess of annual electrical consumption in kWhs
Note on D20: Sums monthly electrical consumption Jan through Dec. Protected cell.
Note on G10: Insert desired % of electrical consumption to be obtained from the PV system.
Note on G12: Value from calculation. Protected cell.
Note on G24: Enter data from "Redbook"
Note on G33: Use CEC Input Values.
Note on G35: Use CEC Input Values.
Note on G40: Be Honest.
Note on G42: Use Pathfinder Mapping.
Note on I19: Calculated value. Protected cell.
Note on I32: From Literature.
Note on K12: Entered value. Protected cell.
Note on K14: Picks larger of Annual Usage or Monthly Usage. Protected cell.
Note on K15: Yearly electrical consumption divided by 12 months for monthly average. Protected cell.
Note on K16: Yearly electrical consumption divided by 365. Protected cell.

## CEC Iverters
CALIFORNIA APPROVED INVERTERS Less than 10kW
Approved
|  |  |  | Power | Weighted | Built-In
Manufacturer Name | Model Number | Description |  | (Watts) | Efficiency | Meter | Notes
< 3kW
Magnetek | PVI-3000-I-OUTD-US (208V) | 3 kW, 150-600 VDC Utility Interactive Inverter | 2262.5 | 2500 | 90.5 | Yes | 2005-08-10
Magnetek | PVI-3000-I-OUTD-US-F (208V) | 3 kW, 150-600 VDC Utility Interactive Inverter | 2443.5 | 2700 | 90.5 | Yes | 2005-08-10
SMA America | SB1100U | 1100W, 240Vac Sunny Boy String Inverter | 1001 | 1100 | 91 | No | 2005-04-01
SMA America | SB1100U-SBD | 1100W, 240Vac Sunny Boy String Inverter | 1001 | 1100 | 91 | Yes | 2005-04-01
SMA America | SB700U | 700W, 120Vac Sunny Boy String Inverter | 636.84 | 696 | 91.5 | No | 2005-09-26
SMA America | SB700U-SBD | 700W, 120Vac Sunny Boy String Inverter with display | 636.84 | 696 | 91.5 | Yes | 2005-04-06
SMA America | SWR1800U | 1.8kW, 120Vac Sunny Boy String Inverter | 1647 | 1800 | 91.5 | No | 2005-04-29
SMA America | SWR1800U-SBD | 1.8W, 120Vac Sunny Boy String Inverter with display | 1647 | 1800 | 91.5 | Yes | 2005-04-29
PV Powered LLC | PVP1800 | 1800W Utility Interactive Inverter | 1656 | 1800 | 92 | Yes | 2005-04-29
Solectria Renewables, LLC | PVI2500-208 | 2500W 208Vac Grid-Tied Solar PV Inverter | 2286.2 | 2485 | 92 | Yes | 2005-09-28
Magnetek | PVI-3000-I-OUTD-US | 3 kW, 150-600 VDC Utility Interactive Inverter | 2318.4 | 2520 | 92 | Yes | 2005-04-05
Solectria Renewables, LLC | PVI1800-240 | 1800W 240Vac Grid-Tied Solar PV Inverter | 1627.075 | 1759 | 92.5 | Yes | 2005-09-28
Solectria Renewables, LLC | PVI1800-208 | 1800W 208Vac Grid-Tied Solar PV Inverter | 1664.075 | 1799 | 92.5 | Yes | 2005-09-28
SMA America | SWR2500U (208V) | 2.1kW, 208Vac Sunny Boy String Inverter | 1942.5 | 2100 | 92.5 | No | 2005-04-29
SMA America | SWR2500U-SBD (208V) | 2.1kW, 208Vac Sunny Boy String Inverter with display | 1942.5 | 2100 | 92.5 | Yes | 2005-04-29
PV Powered LLC | PVP2000 | 2000W (120Vac) Utility Interactive Inverter | 1860 | 2000 | 93 | Yes | 2005-05-30
SunPower Corp. | SPR-2000 | 2000W (120Vac) Utility Interactive Inverter | 1860 | 2000 | 93 | Yes | 2005-05-30
SMA America | SWR2100U | 2.1kW, 240Vac Sunny Boy String Inverter | 1953 | 2100 | 93 | Yes | 2006-03-01
Fronius USA, LLC | IG 2500-LV | 2350W Grid-tied unit with Integrated Disconnects and Performance Meter | 2185.5 | 2350 | 93 | Yes | Upgraded
Solectria Renewables, LLC | PVI2500-240 | 2500W 240Vac Grid-Tied Solar PV Inverter | 2323.14 | 2498 | 93 | Yes | 2005-09-28
SMA America | SWR2500U (240V) | 2.5kW, 240Vac Sunny Boy String Inverter | 2325 | 2500 | 93 | No | 2005-04-29
SMA America | SWR2500U-SBD (240V) | 2.5kW, 240Vac Sunny Boy String Inverter with display | 2325 | 2500 | 93 | Yes | 2005-04-29
Connect Renewable Energy | CE 4000 | 3000W Grid Tied, 240Vac, low dc voltage Inverter | 2650.5 | 2850 | 93 | Yes | 2005-11-21
Fronius USA, LLC | IG 2000 | 2000W Grid-tied unit with Integrated Disconnects and Performance Meter | 1870 | 2000 | 93.5 | Yes | Upgraded
GE Energy | GEPVb-2500-NA-240 | 2.5 kW Brilliance – DC Disconnect - Display | 2350 | 2500 | 94 | Yes | 2006-03-01
Xantrex Technology, Inc. | GT2.5-NA-DS-240 | 2.5 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 2350 | 2500 | 94 | Yes | 2005-09-26
Xantrex Technology, Inc. | GT2.5-NA-DS-240-P | 2.5 kW, 240 Vac, 195-600Vdc Grid Tie Inverter (positive ground) | 2350 | 2500 | 94 | Yes | 2005-09-28
Fronius USA, LLC | IG 3000 | 2700W Grid-tied unit with Integrated Disconnects and Performance Meter | 2538 | 2700 | 94 | Yes | Upgraded
PV Powered LLC | PVP2800-208 | 2800W (208Vac) Utility Interactive Inverter | 2632 | 2800 | 94 | Yes | 2005-04-29
PV Powered LLC | PVP2800-240 | 2800W (240Vac) Utility Interactive Inverter | 2632 | 2800 | 94 | Yes | 2005-04-29
PV Powered LLC | PVP2900-208 or PVP2900 | 2900W (208Vac) Utility Interactive Inverter | 2726 | 2900 | 94 | Yes | 2005-09-26
SunPower Corp. | SPR-2900 | 2900W (208Vac) Utility Interactive Inverter | 2726 | 2900 | 94 | Yes | 2005-04-29
PV Powered LLC | PVP2800-XV | 2800W (240Vac) Utility Interactive Inverter - expanded voltage version | 2646 | 2800 | 94.5 | Yes | 2005-04-29
> 3kW
Xantrex Technology, Inc. | SW4024 | 4.0 kVA, 24Vdc, 120Vac, Trace Engr. batt bkp, sine wave inverter (w/GTI) | 2934.33 | 3297 | 89 | No | 2005-04-01
Beacon Power Corporation | M5 | 5 kW Power Conversion System | 4450 | 5000 | 89 | No | 2005-04-01
Xantrex Technology, Inc. | SW4048 | 4.0 kVA, 48Vdc, 120Vac, Trace Engr. batt bkp, sine wave inverter (w/GTI) | 2905.955 | 3211 | 90.5 | No | 2005-04-01
Alpha Technologies, Inc. | Solaris 3500 | 3.5 kW, 240Vax, 96-200Vdc, NEMA-3R, Grid Interactive PV Inverter, LCD, MPPT | 3124.06 | 3452 | 90.5 | Yes | 2005-04-06
Alpha Technologies, Inc. | Solaris 3500 XP | 3.5 kW, 240 Vac, NEMA-3R, Grid Interactive PV Inverter & Batt. Backed UPS, MPPT | 3167.5 | 3500 | 90.5 | Yes | 2005-04-06
Magnetek | PVI-3000-I-OUTD-US-F (240V) | 3 kW, 150-600 VDC Utility Interactive Inverter | 2730 | 3000 | 91 | Yes | 2005-08-10
OutBack Power Systems | GVFX 3648 | 3600 W Utility Interactive (w/ battery backup) 48vdc Inverter | 2763.67 | 3037 | 91 | No | 2005-04-01
Sharp Corporation | JH-3500U | Utility Interactive Inverter 240Vac L-L, 3.5kW | 3185 | 3500 | 91 | Yes | 2005-08-10
Xantrex Technology, Inc. | SW5548 | 5.5 kVA, 48Vdc, 120Vac, Trace Engr. batt bkp, sine wave inverter (w/GTI) | 3880.24 | 4264 | 91 | No | 2005-04-01
Fronius USA, LLC | IG 4500-LV | 4500W Grid-tied unit with Integrated Disconnects and Performance Meter | 4207.5 | 4500 | 93.5 | Yes | Upgraded
GE Energy | GEPVb-3300-NA-208 | 3.3 kW Brilliance – DC Disconnect - Display | 3102 | 3300 | 94 | Yes | 2006-03-01
Magnetek | PVI-3600-US (208V) | 3.3 kW, 150-600 VDC Utility Interactive Inverter | 3102 | 3300 | 94 | Yes | 2005-12-09
Xantrex Technology, Inc. | GT3.3-NA-DS-208 | 3.3 kW, 208 Vac, 195-600Vdc Grid Tie Inverter | 3102 | 3300 | 94 | Yes | 2005-08-10
Xantrex Technology, Inc. | GT3.3-NA-DS-208-P or POS | 3.3 kW, 208 Vac, 195-600Vdc Grid Tie Inverter | 3102 | 3300 | 94 | Yes | 2005-09-28
SMA America | SB3800U (208V) | 3.5kW, 208Vac Sunny Boy Utility Interactive Inverter with display | 3290 | 3500 | 94 | Yes | 2005-07-13
Fronius USA, LLC | IG 4000 | 4000W Grid-tied unit with Integrated Disconnects and Performance Meter | 3760 | 4000 | 94 | Yes | Upgraded
GE Energy | GEPVb-3000-NA-240 | 3.0 kW Brilliance – DC Disconnect - Display | 2835 | 3000 | 94.5 | Yes | 2006-03-01
Xantrex Technology, Inc. | GT3.0-NA-DS-240 | 3.0 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 2835 | 3000 | 94.5 | Yes | 2005-04-01
Xantrex Technology, Inc. | GT3.0-NA-DS-240-P | 3.0 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 2835 | 3000 | 94.5 | Yes | 2005-11-21
PV Powered LLC | PVP3200-240 or PVP3200 | 3200W (240Vac) Utility Interactive Inverter | 3024 | 3200 | 94.5 | Yes | 2005-09-26
SunPower Corp. | SPR-3200 | 3200W (240Vac) Utility Interactive Inverter | 3024 | 3200 | 94.5 | Yes | 2005-04-29
GE Energy | GEPVb-3300-NA-240 | 3.3 kW Brilliance – DC Disconnect - Display | 3118.5 | 3300 | 94.5 | Yes | 2006-03-01
Magnetek | PVI-3600-OUTD-US-F (208V) | 3.3 kW, 150-600 VDC Utility Interactive Inverter | 3118.5 | 3300 | 94.5 | Yes | 2005-12-09
Xantrex Technology, Inc. | GT3.3-NA-DS-240 | 3.3 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 3118.5 | 3300 | 94.5 | Yes | 2005-08-10
Xantrex Technology, Inc. | GT3.3-NA-DS-240-P or POS | 3.3 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 3118.5 | 3300 | 94.5 | Yes | 2005-09-28
Magnetek | PVI-3600-US (240V) | 3.6 kW, 150-600 VDC Utility Interactive Inverter | 3402 | 3600 | 94.5 | Yes | 2005-12-09
SMA America | SB3800U (240V) | 3.8kW, 240Vac Sunny Boy Utility Interactive Inverter with display | 3591 | 3800 | 94.5 | Yes | 2005-07-13
Fronius USA, LLC | IG 5100 | 5100W Grid-tied unit with Integrated Disconnects and Performance Meter | 4819.5 | 5100 | 94.5 | Yes | Upgraded
SMA America | SB6000U (208V) | 6kW, 208Vac Sunny Boy Utility Interactive Inverter with display | 4914 | 5200 | 94.5 | Yes | 2005-04-01
SMA America | SB6000U (240V) | 6kW, 240Vac Sunny Boy Utility Interactive Inverter with display | 5670 | 6000 | 94.5 | Yes | 2005-04-06
SMA America | SB6000U (277V) | 6kW, 277Vac Sunny Boy Utility Interactive Inverter with display | 5670 | 6000 | 94.5 | Yes | 2005-04-06
Magnetek | PVI-3600-OUTD-US-F (240V) | 3.6 kW, 150-600 VDC Utility Interactive Inverter | 3420 | 3600 | 95 | Yes | 2005-12-09
GE Energy | GEPVb-3800-NA-240 | 3.8 kW Brilliance – DC Disconnect - Display | 3610 | 3800 | 95 | Yes | 2006-03-01
Xantrex Technology, Inc. | GT3.8-NA-DS-240 | 3.8 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 3610 | 3800 | 95 | Yes | 2006-03-01
Xantrex Technology, Inc. | GT3.8-NA-DS-240-P | 3.8 kW, 240 Vac, 195-600Vdc Grid Tie Inverter | 3610 | 3800 | 95 | Yes | 2006-03-01
PV Powered LLC | PVP4600 | 4600W (208Vac) Utility Interactive Inverter | 4393 | 4600 | 95.5 | Yes | 2005-09-26
SunPower Corp. | SPR-4600 | 4600W (208Vac) Utility Interactive Inverter | 4393 | 4600 | 95.5 | Yes | 2005-09-26
PV Powered LLC | PVP5200 | 5200W (240Vac) Utility Interactive Inverter | 4992 | 5200 | 96 | Yes | 2005-09-26
SunPower Corp. | SPR-5200 | 5200W (240Vac) Utility Interactive Inverter | 4992 | 5200 | 96 | Yes | 2005-09-26

## CEC Solar Panels
Manufacturer Name | Rating | Nominal | % | Description
Solar Integrated Technologies | 1544.7 | 1632 | 94.65% | 1632W Flat Plate Single-Ply Roofing Membrane
Solar Integrated Technologies | 1408.2 | 1488 | 94.64% | 1488W Flat Plate Single-Ply Roofing Membrane
Solar Integrated Technologies | 772.4 | 816 | 94.66% | 816W Flat Plate Single-Ply Roofing Membrane
Solar Integrated Technologies | 704.2 | 744 | 94.65% | 744W Flat Plate Single-Ply Roofing Membrane
AstroPower, Inc. | 424.3 | 480 | 88.4% | 480W Single Crystal Large Area Panel, frameless
AstroPower, Inc. | 406.1 | 460 | 88.28% | 460W Single Crystal Large Area Panel, frameless
AstroPower, Inc. | 388.1 | 440 | 88.2% | 440W Single Crystal Large Area Panel, frameless
AstroPower, Inc. | 374.5 | 425 | 88.12% | 425W Single Crystal Large Area Panel, frameless
Solar Integrated Technologies | 352 | 372 | 94.62% | 372W Flat Plate Single-Ply Roofing Membrane
RWE SCHOTT Solar | 297 | 330 | 90% | 330W/50V Crystalline Module, Framed
ASE Americas, Inc. | 283 | 315 | 89.84% | 315W/17V EFG Module, framed
ASE Americas, Inc. | 282.8 | 315 | 89.78% | 315W/50V EFG Module, framed
ASE Americas, Inc. | 269.1 | 300 | 89.7% | 300W/17V EFG Module, framed
ASE Americas, Inc. | 269.1 | 300 | 89.7% | 300W/50V EFG Module, framed
AstroPower, Inc. | 259.2 | 300 | 86.4% | 300W APex Large Area Panel, frameless
ASE Americas, Inc. | 255.4 | 285 | 89.61% | 285W/17V EFG Module, framed
ASE Americas, Inc. | 255.4 | 285 | 89.61% | 285W/50V EFG Module, framed
RWE SCHOTT Solar | 242 | 270 | 89.63% | 270W/17V EFG Module, Framed
RWE SCHOTT Solar | 242 | 270 | 89.63% | 270W/50V EFG Module, Framed
ASE Americas, Inc. | 237 | 265 | 89.43% | 265W/50V EFG Module, framed
ASE Americas, Inc. | 232.6 | 260 | 89.46% | 260W/50V EFG Module, framed
RWE SCHOTT Solar | 223.7 | 250 | 89.48% | 250W/17V EFG Module, Framed
RWE SCHOTT Solar | 223.7 | 250 | 89.48% | 250W/50V EFG Module, Framed
ASE Americas, Inc. | 214.3 | 240 | 89.29% | 240W/42V EFG Module, framed
Evergreen Solar | 213.8 | 240 | 89.08% | 240W String Ribbon poly-Si AC Module (with AES MI-250)
Sunpower Corporation | 190.9 | 210 | 90.9% | 210W Monocrystalline Module
Sanyo Electric Co. Ltd. | 188.7 | 200 | 94.35% | 200W HIT Hybrid a-Si/c-Si Solar Cell Module (A3)
Sanyo Electric Co. Ltd. | 188.7 | 200 | 94.35% | 200W HIT Hybrid a-Si/c-Si Solar Cell Module (A5)
Powerlight Corp. | 184.3 | 205 | 89.9% | 205W Polycrystalline Module
Sanyo Electric Co. Ltd. | 183.5 | 195 | 94.1% | 195W HIT Hybrid a-Si/c-Si Solar Cell Module (A3)
Sanyo Electric Co. Ltd. | 183.5 | 195 | 94.1% | 195W HIT Hybrid a-Si/c-Si Solar Cell Module (A5)
Sharp Corporation | 183.3 | 208 | 88.12% | 208W Multisilicon Module
Sharp Corporation | 180.6 | 205 | 88.1% | 205W Multi-crystalline Silicon Module
Sunpower Corporation | 180 | 200 | 90% | 200W Monocrystalline Module
Powerlight Corp. | 179.7 | 200 | 89.85% | 200W Polycrystalline Module
Sanyo Electric Co. Ltd. | 178.7 | 190 | 94.05% | 190W HIT Hybrid a-Si/c-Si Solar Cell Module
Sanyo Electric Co. Ltd. | 178.7 | 190 | 94.05% | 190W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b.)
Sanyo Electric Co. Ltd. | 178.7 | 190 | 94.05% | 190W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b. w/ addl. wiring)
Sanyo Electric Co. Ltd. | 178.7 | 190 | 94.05% | 190W HIT Hybrid a-Si/c-Si Solar Cell Module (3)
Sanyo Electric Co. Ltd. | 178.7 | 190 | 94.05% | 190W HIT Hybrid a-Si/c-Si Solar Cell Module (5)
Powerlight Corp. | 177.5 | 190 | 93.42% | 190W PowerGuard Roof Tile (Sanyo)
Powerlight Corp. | 177.5 | 190 | 93.42% | 190W PowerGuard Roof Tile (Sanyo)
Powerlight Corp. | 176.1 | 200 | 88.05% | 200W PowerGuard Roof Tile, Frameless
ASE Americas, Inc. | 173.5 | 195 | 88.97% | 195W/34V EFG Module, framed
Sanyo Electric Co. Ltd. | 169.1 | 180 | 93.94% | 180W HIT Hybrid a-Si/c-Si Solar Cell Module
Sanyo Electric Co. Ltd. | 168.1 | 180 | 93.39% | 180W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b.)
Sanyo Electric Co. Ltd. | 168.1 | 180 | 93.39% | 180W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b. w/addl. wiring)
Sanyo Electric Co. Ltd. | 168 | 180 | 93.33% | 180W HIT Hybrid a-Si/c-Si Solar Cell Module (3)
Sanyo Electric Co. Ltd. | 168 | 180 | 93.33% | 180W HIT Hybrid a-Si/c-Si Solar Cell Module (5)
Kyocera Solar, Inc. | 167.7 | 190 | 88.26% | 190W High Efficiency Multicrystal PV Module, Deep Blue
Kyocera Solar, Inc. | 167.4 | 187 | 89.52% | 187W Multicrystal PV Module, Deep Blue
Sharp Corporation | 166.3 | 188 | 88.46% | 188W Single Crystal Silicon Module
BP Solar | 164 | 185 | 88.65% | 185W 24V Saturn Single Crystal Module w/Multicontact conn.
Sharp Corporation | 163.5 | 185 | 88.38% | 185W Single Crystal Silicon Module (same as NT-S5E1U)
Sanyo Electric Co. Ltd. | 163.3 | 175 | 93.31% | 175W HIT Hybrid a-Si/c-Si Solar Cell Module
Sanyo Electric Co. Ltd. | 163.3 | 175 | 93.31% | 175W HIT Hybrid a-Si/c-Si Solar Cell Module (5)
Sanyo Electric Co. Ltd. | 163.3 | 175 | 93.31% | 175W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b.)
Sanyo Electric Co. Ltd. | 163.3 | 175 | 93.31% | 175W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b. w/addl. wiring)
Sharp Corporation | 163.3 | 185 | 88.27% | 185W Multisilicon Module
Powerlight Corp. | 162.2 | 175 | 92.69% | 175W PowerGuard Roof Tile (Sanyo)
BP Solar | 160.2 | 180 | 89% | 180W 24V Saturn Single Crystal Module w/Multicontact conn.
Matrix Solar/Photowatt | 158.3 | 175 | 90.46% | 175W Large Scale Dual Voltage Multi-Si Module
Shell Solar Industries | 158.3 | 175 | 90.46% | 175W High Efficiency Mono-Crystalline Module With Conduit Ready J-Box
Shell Solar Industries | 158.3 | 175 | 90.46% | 175W High Efficiency Mono-Crystalline Module With Quick Connect Cables
Shell Solar Industries | 158.3 | 175 | 90.46% | 175W PowerMax monocrystalline module
Shell Solar Industries | 158.3 | 175 | 90.46% | 175W PowerMax monocrystalline module with Multicontact cable assembly
Sanyo Electric Co. Ltd. | 156.7 | 167 | 93.83% | 167W HIT Hybrid a-Si/c-Si Solar Cell Module
Sanyo Electric Co. Ltd. | 155.8 | 167 | 93.29% | 167W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b.)
Sanyo Electric Co. Ltd. | 155.8 | 167 | 93.29% | 167W HIT Hybrid a-Si/c-Si Solar Cell Module (std. j.b. w/addl. wiring)
BP Solar | 155.2 | 175 | 88.69% | 175W 24V Monocrystalline Module, Multicontact; Bronze frame
BP Solar | 155.2 | 175 | 88.69% | 175W 24V Monocrystalline Module w/Multicontact conn.; Integera frame
BP Solar | 155.2 | 175 | 88.69% | 175W 24V Monocrystalline Module w/Multicontact conn.
BP Solar | 154.9 | 175 | 88.51% | 175W 24V Saturn Single Crystal Module w/Multicontact conn.
RWE SCHOTT Solar | 154.4 | 175 | 88.23% | 175 W Monocrystalline Silicon Module
Sharp Corporation | 154.4 | 175 | 88.23% | 175W Monocrystalline Silicon Module
Sharp Corporation | 154.2 | 175 | 88.11% | 175 W Multisilicon module
AstroPower, Inc. | 154 | 173 | 89.02% | 173W Single Crystal Module w/MC Connectors (was AP-173)
AstroPower, Inc. | 154 | 173 | 89.02% | 173W Single Crystal Module w/MC Connectors (was AP-173) B
GE Energy | 154 | 173 | 89.02% | 173W Single Crystal Module w/MC connectors
GE Energy | 154 | 173 | 89.02% | 173W Single Crystal Module w/MC connectors B
Mitsubishi Electric Corporation | 152.5 | 170 | 89.71% | 170W Polycrystalline lead-free solder module with MC connector
Schuco USA LP | 152.5 | 170 | 89.71% | 170W Polycrystalline Lead-free solder module with MC connector
Powerlight Corp. | 152.3 | 170 | 89.59% | 170W PowerGuard Roof Tile (Two Shell modules)
BP Solar | 151.1 | 170 | 88.88% | 170W 24V Saturn Single Crystal Module w/Multicontact conn.
BP Solar | 150.7 | 170 | 88.65% | 170W 24V Single Crystal Module (universal frame), new AR, Multicontact
BP Solar | 150.7 | 170 | 88.65% | 170W 24V Polycrystalline Module w/Multicontact, Bronze fram
BP Solar | 150.6 | 170 | 88.59% | 170W 24V Polycrystalline Module w/Multicontact conn.; Integra frame
AstroPower, Inc. | 150.1 | 170 | 88.29% | 170W Single Crystal Module
Kyocera Solar, Inc. | 150 | 170 | 88.24% | 170W High Efficiency Multicrystal PV Module, Deep Blue
Pacific Solar Pty Limited | 149.9 | 170 | 88.18% | 170W BP Solar 5170L SunEmpower modular mount
Pacific Solar Pty Limited | 149.9 | 170 | 88.18% | 170W BP Solar 4170L SunEmpower modular mount
Sharp Corporation | 149.9 | 170 | 88.18% | 170W Multisilicon Module
Kyocera Solar, Inc. | 149.6 | 167 | 89.58% | 167W High efficiency Multicrystal PV Module
Shell Solar Industries | 149.1 | 165 | 90.36% | 165W High Efficiency Mono-Crystalline Module With Conduit Ready J-Box
Shell Solar Industries | 149.1 | 165 | 90.36% | 165W High Efficiency Mono-Crystalline Module With Quick Connect Cables
Shell Solar Industries | 149.1 | 165 | 90.36% | 165W PowerMax monocrystalline module
Shell Solar Industries | 149.1 | 165 | 90.36% | 165W PowerMax monocrystalline module with Multicontact cable assembly
Matrix Solar/Photowatt | 149 | 165 | 90.3% | 165W Large Scale Dual Voltage Multi-Si Module
Isofoton | 148.1 | 165 | 89.76% | 165W Monocrystalline Rail Mounted Module
Powerlight Corp. | 148 | 167 | 88.62% | 167W PowerGuard Roof Tile (Kyocera)
Powerlight Corp. | 148 | 170 | 87.06% | 170W Powerguard Roof Tile (Two BP-485L modules)
Sharp Corporation | 147.1 | 167 | 88.08% | 167W Multisilicon module
Sharp Corporation | 147.1 | 167 | 88.08% | 167W Multisilicon module (3)
Sharp Corporation | 147.1 | 167 | 88.08% | 167W Multi-crystalline Silicon Module
Mitsubishi Electric Corporation | 146.9 | 165 | 89.03% | 165W Polycrystalline Lead-free solder module with MC connector
Schuco USA LP | 146.9 | 165 | 89.03% | 165W Polycrystalline Module with Multicontact connectors
AstroPower, Inc. | 146.7 | 165 | 88.91% | 165W Single Cyrstal module w/MC Connectors (was AP-165)
AstroPower, Inc. | 146.7 | 165 | 88.91% | 165W Single Crystal Module w/MC Connectors (was AP-165) B
GE Energy | 146.7 | 165 | 88.91% | 165W Single Crystal Module w/MC connectors
GE Energy | 146.7 | 165 | 88.91% | 165W Single Crystal Module w/MC connectors B
BP Solar | 146.1 | 165 | 88.55% | 165W 24V Monocrystalline Module, Multicontact; Bronze frame
BP Solar | 146.1 | 165 | 88.55% | 165W 24V Monocrystalline Module w/ Multicontact Conn.
Sharp Corporation | 145.4 | 165 | 88.12% | 165W Multisilicon Module (flat screw type)
Sharp Corporation | 145.2 | 165 | 88% | 165W Multisilicon Module (non-flat screw type)
Sharp Corporation | 145.2 | 165 | 88% | 165W Multisilicon Module (flat screw type)
RWE SCHOTT Solar | 144.8 | 165 | 87.76% | 165W Multicrystalline Silicon Module
SunWize Technologies, LLC | 143.9 | 165 | 87.21% | 165W Monocrystalline PV module
Webel-SL Energy Systems | 143.9 | 165 | 87.21% | 165W Monocrystalline PV module
Isofoton | 142.6 | 159 | 89.69% | 159W Monocrystalline Rail Mounted Module
Sharp Corporation | 142.6 | 162 | 88.02% | 162W Multi-crystalline Silicon Module
Mitsubishi Electric Corporation | 142.4 | 160 | 89% | 160W Polycrystalline Lead-free solder module with MC connector
BP Solar | 142.1 | 160 | 88.81% | 160W (2003 Rating) 24V Polycrystalline Module, New AR, Multicontact, Bronze framex
BP Solar | 142.1 | 160 | 88.81% | 160W (2003 Rating) 24V Polycrystalline Module, New AR, Multicontact conn.
BP Solar | 142 | 160 | 88.75% | 160W 16V Polycrystalline Module w/Multicontact conn.
BP Solar | 142 | 160 | 88.75% | 160W 24V Polycrystalline Module w/Multicontact, Bronze frame
Shell Solar Industries | 141.5 | 160 | 88.44% | 160W PowerMax Monocrystalline Module
Shell Solar Industries | 141.5 | 160 | 88.44% | 160W PowerMax Monocrystalline Module w/Multicontact cable assembly
AstroPower, Inc. | 141.1 | 160 | 88.19% | 160W Single Crystal Module
Pacific Solar Pty Limited | 140.9 | 160 | 88.06% | 160W BP Solar 5160L SunEmpower modular mount
Pacific Solar Pty Limited | 140.9 | 160 | 88.06% | 160W BP Solar 4160L SunEmpower modular mount
Pacific Solar Pty Limited | 140.9 | 160 | 88.06% | 160W BP Solar 3160L SunEmpower modular mount
Sharp Corporation | 140.8 | 160 | 88% | 160W Multi-crystalline Silicon Module
Sharp Corporation | 140.8 | 160 | 88% | 160W Multi-crystalline Silicon Module (U3)
Sharp Corporation | 140.6 | 160 | 87.88% | 160W Multisilicon Module
Matrix Solar/Photowatt | 139.9 | 155 | 90.26% | 155W Large Scale Dual Voltage Multi-Si Module
Shell Solar Industries | 139.9 | 155 | 90.26% | 155W High Efficiency Mono-Crystalline Module With Quick Connect Cables
Shell Solar Industries | 139.9 | 155 | 90.26% | 155W PowerMax Monocrystalline Module w/MC Cable Assy
Kyocera Solar, Inc. | 139.7 | 158 | 88.42% | 158W High Efficiency Multicrystal PV Module
SunWize Technologies, LLC | 139.4 | 160 | 87.12% | 160W Monocrystalline PV module
Webel-SL Energy Systems | 139.4 | 160 | 87.12% | 160W Monocrystalline PV module
Powerlight Corp. | 139.2 | 160 | 87% | 160W PowerGuard Roof Tile (BP Solar)
Powerlight Corp. | 139.1 | 160 | 86.94% | 160W PowerGuard Roof Tile (Two BP-380L modules)
Mitsubishi Electric Corporation | 138.8 | 155 | 89.55% | 155W Polycrystalline Lead-free solder module with MC connector
Powerlight Corp. | 138.2 | 158 | 87.47% | 158W PowerGuard Roof Tile (Kyocera)
Powerlight Corp. | 135.3 | 150 | 90.2% | 150W PowerGuard Roof Tile (two Matrix Solar Photowatt modules)
Pacific Solar Pty Limited | 135 | 150 | 90% | 150W Shell Solar SP-150-PL, -PLC SunEmpower modular mount
Shell Solar Industries | 134.9 | 150 | 89.93% | 150W PowerMax mono-cyrstalline module with cable assembly
Siemens Solar Industries | 134.9 | 150 | 89.93% | 150W 24V PowerMax Module
SunWize Technologies, LLC | 134.9 | 155 | 87.03% | 155W Monocrystalline PV module
Webel-SL Energy Systems | 134.9 | 155 | 87.03% | 155W Monocrystalline PV module
Powerlight Corp. | 134.6 | 154 | 87.4% | 154W Double Module PowerGuard Roof Tile (Shell Solar)
Isofoton | 134.3 | 150 | 89.53% | 150W Monocrystalline Rail Mounted Module X2
Isofoton | 134.3 | 150 | 89.53% | 150 W Monocrystalline Rail Mounted Module
Isofoton | 134.3 | 150 | 89.53% | 150W Monocrystalline Rail Mounted Module
Mitsubishi Electric Corporation | 134.2 | 150 | 89.47% | 150W Polycrystalline Lead-free solder module with MC connector
Powerlight Corp. | 133.7 | 150 | 89.13% | 150W PowerGuard Roof Tile (Two Siemens modules)
Powerlight Corp. | 133.6 | 150 | 89.07% | 150W PowerGuard Roof Tile (Siemens)
Powerlight Corp. | 133.5 | 150 | 89% | 150W PowerGuard Roof Tile (Rectangular Siemens)
BP Solar | 133 | 150 | 88.67% | 150W (2003 Rating) 24V Polycrystalline Module, New AR, Multicontact conn.
BP Solar | 132.9 | 150 | 88.6% | 150 W 24V Polycrystalline Module, New AR, Multicontact; Bronze frame
BP Solar | 132.9 | 150 | 88.6% | 150W 24V Polycrystalline Module w/Multicontact, Bronze frame
Pacific Solar Pty Limited | 131.8 | 150 | 87.87% | 150W BP Solar 2150L SunEmpower modular mount
Pacific Solar Pty Limited | 131.8 | 150 | 87.87% | 150W BP Solar 4150L SunEmpower modular mount
Pacific Solar Pty Limited | 131.8 | 150 | 87.87% | 150W BP Solar 3150L SunEmpower modular mount
Shell Solar Industries | 131.7 | 150 | 87.8% | 150W PowerMax monocrystalline module
Shell Solar Industries | 131.7 | 150 | 87.8% | 150W PowerMax monocrystalline module with Multicontact cable assembly
Powerlight Corp. | 131.1 | 150 | 87.4% | 150W PowerGuard Roof Tile (Two Astropower modules)
Shell Solar Industries | 130.7 | 145 | 90.14% | 145W High Efficiency Mono-Crystalline Module With Quick Connect Cables
Shell Solar Industries | 130.7 | 145 | 90.14% | 145W PowerMax Monocrystalline Module w/MC Cable Assy
SunWize Technologies, LLC | 130.5 | 150 | 87% | 150W Monocrystalline PV module
Webel-SL Energy Systems | 130.5 | 150 | 87% | 150W Monocrystalline PV module
Powerlight Corp. | 130.3 | 150 | 86.87% | 150W Power Guard Roof Tile (Shell)
Powerlight Corp. | 129.2 | 150 | 86.13% | 150W PowerGuard Roof Tile (BP Solar)
United Solar Systems Corp. | 128.8 | 136 | 94.71% | 136W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 128.8 | 136 | 94.71% | 136W Field Applied 3J a-Si Laminate
United Solar Systems Corp. | 128.8 | 136 | 94.71% | 136W Structural Standing Seam 3J a-Si Module
ASE Americas, Inc. | 128.5 | 145 | 88.62% | 145W/25V EFG Module, framed
Sharp Corporation | 128.3 | 146 | 87.88% | 146W Multisilicon module
Shell Solar Industries | 125.8 | 140 | 89.86% | 140W PowerMax mono-cyrstalline module with cable assembly
Siemens Solar Industries | 125.8 | 140 | 89.86% | 140W 24V PowerMax Module
Isofoton | 125.1 | 140 | 89.36% | 140W Monocrystalline Rail Mounted Module
Powerlight Corp. | 125.1 | 146 | 85.68% | 146W PowerFuard Roof Tile (Sharp Corp.)
Isofoton | 125 | 140 | 89.29% | 140W Monocrystalline Rail Mounted Module X3
Isofoton | 125 | 140 | 89.29% | 140W Monocrystalline Rail Mounted Module X4
Isofoton | 125 | 140 | 89.29% | 140W Monocrystalline Rail Mounted Module X5
Sharp Corporation | 125 | 142 | 88.03% | 142W Multisilicon Residential Module
BP Solar | 123.8 | 140 | 88.43% | 140W 24V Polycrystalline Module, New AR w/Multicontact; Bronze frame
BP Solar | 123.8 | 140 | 88.43% | 140W 24V Polycrystalline Module, New AR, Multicontact conn.
BP Solar | 123.8 | 140 | 88.43% | 140W 24V Polycrystalline Module w/Multicontact, Bronze frame
Sharp Corporation | 123.2 | 140 | 88% | 140W Multisilicon Residential Module
Shell Solar Industries | 122.8 | 140 | 87.71% | 140W PowerMax monocrystalline module
Shell Solar Industries | 122.8 | 140 | 87.71% | 140W PowerMax monocrystalline module with Multicontact cable assembly
Matrix Solar/Photowatt | 122.2 | 135 | 90.52% | 135W Large Scale Dual Voltage Multi-Si Module
United Solar Systems Corp. | 121.2 | 128 | 94.69% | 128W Field Applied 3J a-Si Laminate, Purlin-Mounted
United Solar Systems Corp. | 121.1 | 128 | 94.61% | 128W Structural Standing Seam 3J a-Si Module, Purlin-Mounted
United Solar Systems Corp. | 121.1 | 128 | 94.61% | 128W Structural Standing Seam 3J a-Si Module w/J-box, Purlin-Mounted
AstroPower, Inc. | 121 | 140 | 86.43% | 140W Apex Silicon Film Module
AstroPower, Inc. | 120.4 | 140 | 86% | 140W Apex Silicon Film module w/MC connectors (was APx-140)
AstroPower, Inc. | 120.4 | 140 | 86% | 140W Apex Silicon Film module w/MC connectors (was APx-140) B
AstroPower, Inc. | 120.4 | 140 | 86% | 140W Apex Silicon Film module w/o connectors (was APx-140)
AstroPower, Inc. | 120.4 | 140 | 86% | 140W Apex Silicon Film module w/o connectors (was APx-140)B
Powerlight Corp. | 119.8 | 135 | 88.74% | 135W (2003 Rating) PowerGuard Roof Tile (Siemens)
Powerlight Corp. | 119.1 | 135 | 88.22% | 135W (Pre-2003 Rating) PowerGuard Roof Tile (Siemens)
United Solar Systems Corp. | 118.4 | 128 | 92.5% | 128W Field Applied 3J a-Si Laminate, Deck-Mounted
United Solar Systems Corp. | 118.3 | 128 | 92.42% | 128W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 118.3 | 128 | 92.42% | 128W Structural Standing Seam 3J a-Si Module, Deck-Mounted
United Solar Systems Corp. | 118.3 | 128 | 92.42% | 128W Structural Standing Seam 3J a-Si Module w/J-box, Deck-Mounted
United Solar Systems Corp. | 117.4 | 124 | 94.68% | 124W a-Si Module with Black Anodized Frame
United Solar Systems Corp. | 117.4 | 124 | 94.68% | 124W Field Applied 3J a-Si Laminate
Siemens Solar Industries | 116.7 | 130 | 89.77% | 130W 24V PowerMax Module
Shell Solar Industries | 116.6 | 130 | 89.69% | 130W PowerMax mono-cyrstalline module with cable assembly
Isofoton | 116 | 130 | 89.23% | 130W Monocrystalline Rail Mounted Module
Isofoton | 116 | 130 | 89.23% | 130W Monocrystalline Rail Mounted Module X2
Mitsubishi Electric Corporation | 115.2 | 130 | 88.62% | 130 W Polycrystalline Module with Multicontact connectors
Mitsubishi Electric Corporation | 115.2 | 130 | 88.62% | 130W Polycrystalline Lead-free solder module with MC connector
Schuco USA LP | 115.2 | 130 | 88.62% | 130W Polycrystalline Module with Multicontact connectors
Powerlight Corp. | 115.1 | 130 | 88.54% | 130W PowerGuard Roof Tile (Astropower AP-130)
United Solar Systems Corp. | 113.5 | 120 | 94.58% | 120W Structural Standing Seam 3J a-Si Module, Purlin-Mounted
United Solar Systems Corp. | 113.5 | 120 | 94.58% | 120W Structural Standing Seam 3J a-Si Module w/J-box, Purlin-Mounted
Matrix Solar/Photowatt | 112.9 | 125 | 90.32% | 125W Large Scale Dual Voltage Multi-Si Module
AstroPower, Inc. | 112.2 | 130 | 86.31% | 130W Apex Silicon Film Module
Kaneka Corporation | 111.9 | 120 | 93.25% | 120W a-Si twin type module (TSC)
Kaneka Corporation | 111.9 | 120 | 93.25% | 120W a-Si module (TSC)
Kaneka Corporation | 111.9 | 120 | 93.25% | 120W a-Si twin type module (TSD)
Kaneka Corporation | 111.9 | 120 | 93.25% | 120W a-Si module (TSD)
Kyocera Solar, Inc. | 111.8 | 125 | 89.44% | 125W High efficiency Multicrystal PV Module
AstroPower, Inc. | 111.6 | 130 | 85.85% | 130W Apex Silicon Film module w/MC connectors (was APx-130)
AstroPower, Inc. | 111.6 | 130 | 85.85% | 130W Apex Silicon Film module w/MC connectors (was APx-130) B
AstroPower, Inc. | 111.6 | 130 | 85.85% | 130W Apex Silicon Film module w/o connectors (was APx-130)
AstroPower, Inc. | 111.6 | 130 | 85.85% | 130W Apex Silicon Film module w/o connectors (was APx-130) B
United Solar Systems Corp. | 110.9 | 120 | 92.42% | 120W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 110.9 | 120 | 92.42% | 120W Structural Standing Seam 3J a-Si Module, Deck-Mounted
United Solar Systems Corp. | 110.9 | 120 | 92.42% | 120W Structural Standing Seam 3J a-Si Module w/J-box, Deck-Mounted
BP Solar | 110.8 | 125 | 88.64% | 125W 12V Polycrystalline Module w/Multicontact conn.
BP Solar | 110.8 | 125 | 88.64% | 125W 12V Polycrystalline Module, universal frame
Powerlight Corp. | 110.8 | 125 | 88.64% | 125W PowerGuard Roof Tile (Kyocera)
Mitsubishi Electric Corporation | 110.7 | 125 | 88.56% | 125 W Polycrystalline Module with Multicontact connectors
Mitsubishi Electric Corporation | 110.7 | 125 | 88.56% | 125W Polycrystalline Lead-free solder module with MC connector
Kyocera Solar, Inc. | 110.3 | 125 | 88.24% | 125W High Efficiency Multicrystal PV Module, Deep Blue
Sharp Corporation | 110.1 | 125 | 88.08% | 125W Multisilicon Module (flat screw type)
Sharp Corporation | 110 | 125 | 88% | 125W Multisilicon Module (non-flat screw type, black color frame)
United Solar Systems Corp. | 109.9 | 116 | 94.74% | 116W Field Applied 3J a-Si Laminate, Purlin-Mounted
United Solar Systems Corp. | 109.9 | 116 | 94.74% | 116W Framed Triple-Junction a-Si Module
United Solar Systems Corp. | 109.8 | 116 | 94.66% | 116W a-Si Module with Black Anodized Frame
Sharp Corporation | 108.3 | 123 | 88.05% | 123W Multisilicon Module
Sharp Corporation | 108.3 | 123 | 88.05% | 123W Multisilicon Module (w/junction box)
Sharp Corporation | 108.3 | 123 | 88.05% | 123W Multisilicon Module (w/junct box)
Kaneka Corporation | 108.2 | 116 | 93.28% | 116W a-Si Twin Type Module
Kaneka Corporation | 108.2 | 116 | 93.28% | 116W a-Si Twin Type Module B
RWE SCHOTT Solar | 107.8 | 123 | 87.64% | 123W Multisilicon Module
Mitsubishi Electric Corporation | 107.6 | 120 | 89.67% | 120W Polycrystalline Lead-free solder w/o Cable
United Solar Systems Corp. | 107.4 | 116 | 92.59% | 116W Field Applied 3J a-Si Laminate, Deck-Mounted
AstroPower, Inc. | 106 | 120 | 88.33% | 120W Single Crystal Module (was AP-1206)
AstroPower, Inc. | 106 | 120 | 88.33% | 120W Single Crystal Module
Kyocera Solar, Inc. | 105.7 | 120 | 88.08% | 120W High Efficiency Multicrystal PV Module
Baoding Yingli New Energy | 105.6 | 120 | 88% | 120W Crystalline Silicon Solar Cells
Midway Labs, Inc. | 105 | 115 | 91.3% | 115W Concentrator (335x) Module
SunWize Technologies, LLC | 105 | 120 | 87.5% | 120W Monocrystalline PV Module
Webel-SL Energy Systems | 105 | 120 | 87.5% | 120W Monocrystalline PV Module
Powerlight Corp. | 104.9 | 120 | 87.42% | 120W PowerGuard Roof Tile (Astropower)
Powerlight Corp. | 103.8 | 120 | 86.5% | 120W PowerGuard Roof Tile (Kyocera)
Matrix Solar/Photowatt | 103.7 | 115 | 90.17% | 115W Large Scale Dual Voltage Multi-Si Module
Powerlight Corp. | 103.7 | 120 | 86.42% | 120W PowerGuard Roof Tile (Solarex poly-Si)
Evergreen Solar | 103.1 | 115 | 89.65% | 115W String Ribbon Cedar Line Module
BP Solar | 101.7 | 115 | 88.43% | 115W 12V Polycrystalline Module w/Multicontact conn.
BP Solar | 101.7 | 115 | 88.43% | 115W 12V Polycrystalline Module, universal frame
SunWize Technologies, LLC | 100.5 | 115 | 87.39% | 115W Monocrystalline PV Module
Webel-SL Energy Systems | 100.5 | 115 | 87.39% | 115W Monocrystalline PV Module
Evergreen Solar | 99.7 | 112 | 89.02% | 112W String Ribbon poly-Si AC Module (with Trace MS100)
Shell Solar Industries | 99.2 | 110 | 90.18% | 110W PowerMax Module
Isofoton | 98.7 | 110 | 89.73% | 110W Monocrystalline Rail Mounted Module X2
Isofoton | 98.7 | 110 | 89.73% | 110W Monocrystalline Rail Mounted Module
Evergreen Solar | 98.4 | 110 | 89.45% | 110W Cedar Line module
Mitsubishi Electric Corporation | 98.4 | 110 | 89.45% | 110W Polycrystalline Lead-free solder w/o Cable
AstroPower, Inc. | 97.8 | 110 | 88.91% | 110W Single Cyrstal Module w/o connectors (was AP-110) B
AstroPower, Inc. | 97.8 | 110 | 88.91% | 110W Single Cyrstal Module w/MC connectors (was AP-110)
AstroPower, Inc. | 97.8 | 110 | 88.91% | 110W Single Cyrstal Module w/MC connectors (was AP-110) B
AstroPower, Inc. | 97.8 | 110 | 88.91% | 110W Single Crystal Module w/o connectors (was AP-110)
GE Energy | 97.8 | 110 | 88.91% | 110W Single Crystal Module w/MC connectors
GE Energy | 97.8 | 110 | 88.91% | 110W Single Crystal Module w/MC connectors B
GE Energy | 97.8 | 110 | 88.91% | 110W Single Crystal Module w/o connectors
GE Energy | 97.8 | 110 | 88.91% | 110W Single Crystal Module w/o connectors B
AstroPower, Inc. | 97 | 110 | 88.18% | 110W Single Crystal Module (was AP-1106)
AstroPower, Inc. | 97 | 110 | 88.18% | 110W Single Crystal Module
Baoding Yingli New Energy | 96.6 | 110 | 87.82% | 110W Crystalline Silicon Solar Cells
SunWize Technologies, LLC | 96 | 110 | 87.27% | 110W Monocrystalline PV Module
Webel-SL Energy Systems | 96 | 110 | 87.27% | 110W Monocrystalline PV Module
Isofoton | 95 | 106 | 89.62% | 106W Monocrystalline Rail Mounted Module
Isofoton | 95 | 106 | 89.62% | 106W Monocrystalline Rail Mounted Module X2
Matrix Solar/Photowatt | 94.6 | 105 | 90.1% | 105W Large Scale Dual Voltage multi-Si Module
Powerlight Corp. | 93.7 | 110 | 85.18% | 110W PowerGuard Roof Tile (AstroPower)
Evergreen Solar | 91.2 | 102 | 89.41% | 102W Cedar Line module
Matrix Solar/Photowatt | 90 | 100 | 90% | 100W Large Scale Dual Voltage multi-Si Module
ASE Americas, Inc. | 89.7 | 100 | 89.7% | 100W/17V EFG Module, framed
Isofoton | 89.5 | 100 | 89.5% | 100W Monocrystalline Rail Mounted Module X2
Isofoton | 89.5 | 100 | 89.5% | 100W Monocrystalline Rail Mounted Module
AstroPower, Inc. | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/MC connectors (was AP-100)
AstroPower, Inc. | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/MC connectors (was AP-100) B
AstroPower, Inc. | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/o connectors (was AP-100)
AstroPower, Inc. | 88.7 | 100 | 88.7% | 100 W Single Crystal Module w/o connectors (was AP-100) B
GE Energy | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/MC connectors
GE Energy | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/MC connectors B
GE Energy | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/o connectors
GE Energy | 88.7 | 100 | 88.7% | 100W Single Crystal Module w/o connectors B
Powerlight Corp. | 88.6 | 100 | 88.6% | 100W PowerGuard Roof Tile (ASE Americas)
United Solar Systems Corp. | 88.1 | 93 | 94.73% | 93W Field Applied 3J a-Si Laminate
AstroPower, Inc. | 88 | 100 | 88% | 100W Single Crystal Module (was AP-1006)
AstroPower, Inc. | 88 | 100 | 88% | 100W Single Crystal Module
SunWize Technologies, LLC | 87.1 | 100 | 87.1% | 100W Monocrystalline PV Module
Webel-SL Energy Systems | 87.1 | 100 | 87.1% | 100W Monocrystalline PV Module
Solec International, Inc. | 86.5 | 100 | 86.5% | 100W Dual Voltage Crystalline Solar Electric Module
Matrix Solar/Photowatt | 85.4 | 95 | 89.89% | 95W Large Scale Dual Voltage multi-Si Module
Isofoton | 84.2 | 94 | 89.57% | 94W Monocrystalline Rail Mounted Module X2
Isofoton | 84.2 | 94 | 89.57% | 94W Monocrystalline Rail Mounted Module
Evergreen Solar | 83.9 | 94 | 89.26% | 94W Cedar Line module
SunWize Technologies, LLC | 82.8 | 95 | 87.16% | 95W Monocrystalline PV Module
United Solar Systems Corp. | 82.5 | 87 | 94.83% | 87W Field Applied 3J a-Si Laminate, Purlin-Mounted
Sunpower Corporation | 81.8 | 90 | 90.89% | 90W Monocrystalline Module
Matrix Solar/Photowatt | 81.2 | 90 | 90.22% | 90W Large Scale multi-Si Module
Matrix Solar/Photowatt | 80.9 | 90 | 89.89% | 90W Large Scale Dual Voltage multi-Si Module
United Solar Systems Corp. | 80.6 | 87 | 92.64% | 87W Field Applied 3J a-Si Laminate, Deck-Mounted
MC Solar | 80.4 | 90 | 89.33% | 90W Thin-film CdTe Laminate w/ Mounting Brackets
MC Solar | 80.4 | 90 | 89.33% | 90W Thin-film CdTe Laminate w/ Mounting Brackets (now BP990B)
BP Solar | 80 | 90 | 88.89% | 90W 12V Saturn Single Crystal Module, dark frame
BP Solar | 80 | 90 | 88.89% | 90W 12V Saturn Single Crystal Module w/Multicontact conn.
BP Solar | 80 | 90 | 88.89% | 90W 12V Saturn Single Crystal Module, universal frame
SunWize Technologies, LLC | 78.4 | 90 | 87.11% | 90W Monocrystalline PV Module
Webel-SL Energy Systems | 78.4 | 90 | 87.11% | 90W Monocrystalline PV Module
AstroPower, Inc. | 77.8 | 90 | 86.44% | 90W APex Module
Kyocera Solar, Inc. | 77.8 | 88 | 88.41% | 88W Light-transmitting Multicrystal PV Module, Deep Blue
Solec International, Inc. | 77.8 | 90 | 86.44% | 90W Framed Crystalline Solar Electric Module
Shell Solar Industries | 76.9 | 85 | 90.47% | 85W High Efficiency Mono-Crystalline Module With Conduit Ready J-Box
Shell Solar Industries | 76.9 | 85 | 90.47% | 85W PowerMax monocrystalline module
BP Solar | 75.5 | 85 | 88.82% | 85W 12V Saturn Single Crystal Module w/Multicontact conn.
BP Solar | 75.3 | 85 | 88.59% | 85W Single Cyrstal Module (universal frame), new AR
BP Solar | 75.3 | 85 | 88.59% | 85W Single Crystal Module (universal frame), new AR, Multicontact
BP Solar | 75.3 | 85 | 88.59% | 85W Single Crystal Module (universal frame), new AR
Baoding Yingli New Energy | 74.9 | 85 | 88.12% | 85W Crystalline Silicon Solar Cells
SunWize Technologies, LLC | 73.9 | 85 | 86.94% | 85W Monocrystalline PV Module
Webel-SL Energy Systems | 73.9 | 85 | 86.94% | 85W Monocrystalline PV Module
Shell Solar Industries | 72.3 | 80 | 90.38% | 80W High Efficiency Mono-Crystalline Module With Conduit Ready J-Box
Shell Solar Industries | 72.3 | 80 | 90.38% | 80W PowerMax monocrystalline module
Matrix Solar/Photowatt | 72 | 80 | 90% | 80W Large Scale multi-Si Module
MC Solar | 71.3 | 80 | 89.12% | 80W Thin-film CdTe Laminate w/ Mounting Brackets
MC Solar | 71.3 | 80 | 89.12% | 80W Thin-film CdTe Laminate w/ Mounting Brackets (now BP980B)
BP Solar | 71 | 80 | 88.75% | 80W (2003 Rating) Polycrystalline Module (universal frame), new AR, Multicontact conn.
BP Solar | 71 | 80 | 88.75% | 80W (2003 Rating) Polycrystalline Module (universal frame), new AR
BP Solar | 70.8 | 80 | 88.5% | 80W (2003 Rating) Single Crystal Module (universal frame), new AR, Multicontact conn.
BP Solar | 70.8 | 80 | 88.5% | 80W (2003 Rating) Single Crystal Module (universal frame), new AR
Shell Solar Industries | 70.8 | 80 | 88.5% | 80W PowerMax Monocrystalline Module
Powerlight Corp. | 70.7 | 80 | 88.38% | 80W PowerGuard Roof Tile (BP Solar)
Kyocera Solar, Inc. | 70.4 | 80 | 88% | 80W High Efficiency Multicrystal PV Module (01)
Kyocera Solar, Inc. | 70.4 | 80 | 88% | 80W High Efficiency Multicrystal PV Module
Sharp Corporation | 70.4 | 80 | 88% | 80W Multisilicon Module
Sharp Corporation | 70.4 | 80 | 88% | 80W Multisilicon Module (w/junction box)
Sharp Corporation | 70.4 | 80 | 88% | 80W Multisilicon Module (w/junct box)
RWE SCHOTT Solar | 70.2 | 80 | 87.75% | 80W Multisilicon Module
Webel-SL Energy Systems | 69.5 | 80 | 86.88% | 80W Monocrystalline PV Module
AstroPower, Inc. | 69.2 | 80 | 86.5% | 80W APex Module
Solec International, Inc. | 68.9 | 80 | 86.12% | 80W Framed Crystalline Solar Electric Module
Matrix Solar/Photowatt | 67.5 | 75 | 90% | 75W Large Scale multi-Si Module
Isofoton | 67.1 | 75 | 89.47% | 75W Monocrystalline Rail Mounted Module
Powerlight Corp. | 66.8 | 75 | 89.07% | 75W PowerGuard Roof Tile (Siemens)
Spire Solar Chicago | 66.7 | 75 | 88.93% | 75W Rail Mounted Monocrystalline Module
Spire Solar Chicago | 66.7 | 75 | 88.93% | 75W Rail Mounted Monocrystalline Module x
BP Solar | 66.4 | 75 | 88.53% | 75W (2003 Rating) Polycrystalline Module (universal frame), new AR, Multicontact conn.
BP Solar | 66.4 | 75 | 88.53% | 75W (2003 Rating) Polycrystalline Module (universal frame), new AR
BP Solar | 66.3 | 75 | 88.4% | 75W (2003 Rating) Single Crystal Module (universal frame), new AR, Multicontact conn.
BP Solar | 66.3 | 75 | 88.4% | 75W (2003 Rating) Single Crystal Module (universal frame), new AR
AstroPower, Inc. | 66.2 | 75 | 88.27% | 75W Single Crystal Module (was AP-7105)
AstroPower, Inc. | 66.2 | 75 | 88.27% | 75W Single Crystal Module
Baoding Yingli New Energy | 65.9 | 75 | 87.87% | 75W Crystalline Silicon Solar Cells
Shell Solar Industries | 65.9 | 75 | 87.87% | 75W PowerMax monocrystalline module
Powerlight Corp. | 65.1 | 75 | 86.8% | 75W Power Guard Roof Tile (Shell)
SunWize Technologies, LLC | 65.1 | 75 | 86.8% | 75W Monocrystalline PV Module
Webel-SL Energy Systems | 65.1 | 75 | 86.8% | 75W Monocrystalline PV Module
AstroPower, Inc. | 64.8 | 75 | 86.4% | 75W Apex Module
AstroPower, Inc. | 64.8 | 75 | 86.4% | 75W APex Module
AstroPower, Inc. | 64.4 | 75 | 85.87% | 75W Apex Module w/o connectors (was APx-75)
AstroPower, Inc. | 64.4 | 75 | 85.87% | 75W Apex Module w/o connectors (was APx-75) B
United Solar Systems Corp. | 64.4 | 68 | 94.71% | 68W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 64.4 | 68 | 94.71% | 68W Field Applied 3J a-Si Laminate
United Solar Systems Corp. | 64.4 | 68 | 94.71% | 68WStructural Standing Seam 3J a-Si Module
Sharp Corporation | 63 | 72 | 87.5% | 72W Multi-crystalline Silicon Module (right)
Sharp Corporation | 63 | 72 | 87.5% | 72W Multi-crystalline Silicon Module (left)
Matrix Solar/Photowatt | 62.9 | 70 | 89.86% | 70W Large Scale multi-Si Module
Isofoton | 62.5 | 70 | 89.29% | 70W Monocrystalline Rail Mounted Module
Isofoton | 62.5 | 70 | 89.29% | 70W Monocrystalline Rail Mounted Module X2
MC Solar | 62.3 | 70 | 89% | 70W Thin-film CdTe Laminate w/ Mounting Brackets
AstroPower, Inc. | 62.2 | 70 | 88.86% | 70W Single Crystal Module w/o connectors (was AP-70)
AstroPower, Inc. | 62.2 | 70 | 88.86% | 70W Single Cyrstal Module w/o connectors (was AP-70) B
GE Energy | 62.2 | 70 | 88.86% | 70W Single Crystal Module w/o connectors
GE Energy | 62.2 | 70 | 88.86% | 70W Single Crystal Module w/o connectors B
Kyocera Solar, Inc. | 61.6 | 70 | 88% | 70W High Efficiency Multicrystal PV Module
Shell Solar Industries | 61.4 | 70 | 87.71% | 70W PowerMax monocrystalline module
Sharp Corporation | 61.2 | 70 | 87.43% | 70W Multi-crystalline Silicon Module (right)
Sharp Corporation | 61.2 | 70 | 87.43% | 70W Multi-crystalline Silicon Module (left)
United Solar Systems Corp. | 60.6 | 64 | 94.69% | 64W Structural Standing Seam 3J a-Si Module, Purlin-Mounted
United Solar Systems Corp. | 60.6 | 64 | 94.69% | 64W Structural Standing Seam 3J a-Si Module w/J-box, Purlin-Mounted
United Solar Systems Corp. | 60.6 | 64 | 94.69% | 64W Field Applied 3J a-Si Laminate, Purlin-Mounted
United Solar Systems Corp. | 60.6 | 64 | 94.69% | 64W Framed Triple-Junction a-Si Module
AstroPower, Inc. | 60.1 | 70 | 85.86% | 70W Apex Module w/o connectos (was APx-70)
AstroPower, Inc. | 60.1 | 70 | 85.86% | 70W Apex Module w/o connectos (was APx-70) B
United Solar Systems Corp. | 59.2 | 64 | 92.5% | 64W Field Applied 3J a-Si Laminate, Deck-Mounted
United Solar Systems Corp. | 59.1 | 64 | 92.34% | 64W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 59.1 | 64 | 92.34% | 64W Structural Standing Seam 3J a-Si Module, Deck-Mounted
United Solar Systems Corp. | 59.1 | 64 | 92.34% | 64W Structural Standing Seam 3J a-Si Module w/J-box, Deck-Mounted
United Solar Systems Corp. | 58.7 | 62 | 94.68% | 62W a-Si Module with Black Anodized Frame
United Solar Systems Corp. | 58.7 | 62 | 94.68% | 62W Field Applied 3J a-Si Laminate
Isofoton | 58 | 65 | 89.23% | 65W Monocrystalline Rail Mounted Module
AstroPower, Inc. | 57.7 | 65 | 88.77% | 65W Single Crystal Module w/o connectors (was AP-65)
AstroPower, Inc. | 57.7 | 65 | 88.77% | 65W Single Crystal Module w/o connectors (was AP-65) B
GE Energy | 57.7 | 65 | 88.77% | 65W Single Crystal Module w/o connectors
GE Energy | 57.7 | 65 | 88.77% | 65W Single Crystal Module w/o connectors B
BP Solar | 57.6 | 60 | 96% | 65W 12V Polycrystalline Module, universal frame
Powerlight Corp. | 57.4 | 63 | 91.11% | 63W Sun Tile
AstroPower, Inc. | 57.2 | 65 | 88% | 65W Single Crystal Module (was AP-6105)
AstroPower, Inc. | 57.2 | 65 | 88% | 65W Single Crystal Module
BP Solar | 57.2 | 60 | 95.33% | 65W 6V Polycrystalline Module w/MC, Roof Tile Frame
First Solar, LLC | 57.2 | 60 | 95.33% | 60W Thin Film CdTe laminate
First Solar, LLC | 57.2 | 60 | 95.33% | 60W Thin Film CdTe module with mounting rails
United Solar Systems Corp. | 56.8 | 60 | 94.67% | 60W Structural Standing Seam 3J a-Si Module, Purlin-Mounted
United Solar Systems Corp. | 56.8 | 60 | 94.67% | 60W Structural Standing Seam 3J a-Si Module w/J-box, Purlin-Mounted
United Solar Systems Corp. | 56.8 | 60 | 94.67% | 60W Framed Triple-Junction a-Si Module
Powerlight Corp. | 56.6 | 65 | 87.08% | One Astropower AP-65 laminate mounted on one PowerGuard backerboard
AstroPower, Inc. | 56 | 65 | 86.15% | 65W Apex Module
Kaneka Corporation | 56 | 60 | 93.33% | 60W a-Si module
Kaneka Corporation | 56 | 60 | 93.33% | 60W a-Si module (GSA221)
AstroPower, Inc. | 55.7 | 65 | 85.69% | 65W Apex Module w/o connectors (was APx-65)
AstroPower, Inc. | 55.7 | 65 | 85.69% | 65W Apex Module w/o connectors (was APx-65) B
United Solar Systems Corp. | 55.4 | 60 | 92.33% | 60W Arch. Standing Seam 3J a-Si Module
United Solar Systems Corp. | 55.4 | 60 | 92.33% | 60W Structural Standing Seam 3J a-Si Module, Deck-Mounted
United Solar Systems Corp. | 55.4 | 60 | 92.33% | 60W Structural Standing Seam 3J a-Si Module w/J-box, Deck-Mounted
United Solar Systems Corp. | 55 | 58 | 94.83% | 58W Field Applied 3J a-Si Laminate, Purlin-Mounted
United Solar Systems Corp. | 54.9 | 58 | 94.66% | 58W a-Si Module with Black Anodized Frame
Sharp Corporation | 54.5 | 62 | 87.9% | 62W Multi-crystalline Silicon Module
Kaneka Corporation | 54.1 | 58 | 93.28% | 58W a-Si module
Kaneka Corporation | 54.1 | 58 | 93.28% | 58W a-Si module (CSA)
Kaneka Corporation | 54.1 | 58 | 93.28% | 58W a-Si module (CSB)
Kaneka Corporation | 54.1 | 58 | 93.28% | 58W a-Si module
United Solar Systems Corp. | 53.7 | 58 | 92.59% | 58W Field Applied 3J a-Si Laminate, Deck-Mounted
Evergreen Solar | 53.4 | 60 | 89% | 60W String Ribbon poly-Si Module
BP Solar | 53 | 60 | 88.33% | 60W 12V Polycrystalline Module, universal frame
Kyocera Solar, Inc. | 52.7 | 60 | 87.83% | 60W High Efficiency Multicrystal PV Module
Sharp Corporation | 52.7 | 60 | 87.83% | 60W Multi-crystalline Silicon Module
First Solar, LLC | 52.4 | 55 | 95.27% | 55W Thin-Film CdTe Laminate
First Solar, LLC | 52.4 | 55 | 95.27% | 55W Thin-Film CdTe Module w/ D-channel mounting rails
BP Solar | 51.9 | 55 | 94.36% | 55W Millennia 2J a-Si Module (med. Voltage, universal frame)
Evergreen Solar | 49.8 | 56 | 88.93% | 56W String Ribbon poly-Si Module
Siemens Solar Industries | 49.6 | 55 | 90.18% | 55W PowerMax module
Isofoton | 49.4 | 55 | 89.82% | 55W Monocrystalline Rail Mounted Module
Evergreen Solar | 49.2 | 55 | 89.45% | 55W Cedar Line module
AstroPower, Inc. | 48.9 | 55 | 88.91% | 55W Single Crystal Module w/MC connectors (was AP-55-GT)
AstroPower, Inc. | 48.9 | 55 | 88.91% | 55W Single Crystal Module w/MC connectors (was AP-55-GA)
GE Energy | 48.9 | 55 | 88.91% | 55W Single Crystal Module w/MC connectors
GE Energy | 48.9 | 55 | 88.91% | 55W Single Crystal Module w/MC connectors B
AstroPower, Inc. | 48.5 | 55 | 88.18% | 55W Single Crystal Module
AstroPower, Inc. | 48.5 | 55 | 88.18% | 55W Single Crystal Module
Solec International, Inc. | 47.7 | 55 | 86.73% | 55W Framed Crystalline Solar Electric Module
First Solar, LLC | 47.6 | 50 | 95.2% | 50W Thin Film CdTe Module with mounting rails
First Solar, LLC | 47.6 | 50 | 95.2% | 50W/65V Thin Film CdTe laminate
First Solar, LLC | 47.6 | 50 | 95.2% | 50W/65V Thin Film CdTe laminate w/ C-channel mounting rails
First Solar, LLC | 47.6 | 50 | 95.2% | 50W/65V Thin Film CdTe laminate w/ Z-channel mounting rails
Isofoton | 47.5 | 53 | 89.62% | 53W Monocrystalline Rail Mounted Module
Kyocera Solar, Inc. | 47.5 | 53 | 89.62% | 53W Multicrystal PV Module, Deep Blue, Meridian Frame
Kyocera Solar, Inc. | 47.5 | 53 | 89.62% | 53W Multicrystal PV Module, Deep Blue, Samurai Frame
Powerlight Corp. | 47.4 | 50 | 94.8% | 50W PowerGuard Roof Tile (First Solar)
Evergreen Solar | 45.6 | 51 | 89.41% | 51W Cedar Line module
Siemens Solar Industries | 45 | 50 | 90% | 50W PowerMax Module
Isofoton | 44.8 | 50 | 89.6% | 50W Monocrystalline Rail Mounted Module
Evergreen Solar | 44.4 | 50 | 88.8% | 50W String Ribbon poly-Si Module
AstroPower, Inc. | 44.2 | 50 | 88.4% | 50W Single Crystal Module w/o connectors (was AP-50)
AstroPower, Inc. | 44.2 | 50 | 88.4% | 50W Single Crystal Module w/o connectors (was AP-50) B
GE Energy | 44.2 | 50 | 88.4% | 50W Single Crystal Module w/o connectors
GE Energy | 44.2 | 50 | 88.4% | 50W Single Crystal Module w/o connectors B
Astropower, Inc. | 44 | 50 | 88% | 50W Single Crystal Module
AstroPower, Inc. | 44 | 50 | 88% | 50W Single Crystal Module
Baoding Yingli New Energy | 43.9 | 50 | 87.8% | 50W Crystalline Silicon Solar Cells
Kyocera Solar, Inc. | 43.9 | 50 | 87.8% | 50W High Efficiency Multicrystal PV Module
AstroPower, Inc. | 43.2 | 50 | 86.4% | 50W Apex Module
AstroPower, Inc. | 42.9 | 50 | 85.8% | 50W Apex Module w/o connectors (was APx-50)
AstroPower, Inc. | 42.9 | 50 | 85.8% | 50W Apex Module w/o connectors (was APx-50) B
First Solar, LLC | 42.8 | 45 | 95.11% | 45W Thin Film CdTe laminate
First Solar, LLC | 42.8 | 45 | 95.11% | 45W Thin Film CdTe module with mounting rails
Evergreen Solar | 41.9 | 47 | 89.15% | 47W Cedar Line module
Siemens Solar Industries | 41.5 | 46 | 90.22% | 46W PowerMax Module
Powerlight Corp. | 40.5 | 43 | 94.19% | 43W PowerGuard Roof Tile (Solarex a-Si)
United Solar Systems Corp. | 39.8 | 42 | 94.76% | 42W Framed Triple-Junction a-Si Module
AstroPower, Inc. | 39.7 | 45 | 88.22% | 45W Single Crystal Module w/o connectors (was AP-45)
AstroPower, Inc. | 39.7 | 45 | 88.22% | 45W Single Crystal Moduel w/o connectors (was AP-45) B
GE Energy | 39.7 | 45 | 88.22% | 45W Single Crystal Module w/o connectors
GE Energy | 39.7 | 45 | 88.22% | 45W Single Crystal Module w/o connectors B
AstroPower, Inc. | 38.8 | 45 | 86.22% | 45W Apex Module
AstroPower, Inc. | 38.6 | 45 | 85.78% | 45W Apex Module w/o connectors (was APx-45)
AstroPower, Inc. | 38.6 | 45 | 85.78% | 45W Apex Module w/o connectors (was APx-45) B
Dunasolar Inc. | 38.4 | 40 | 96% | 40W Unframed 2J a-Si Module
Energy Photovoltaics, Inc. | 38.4 | 40 | 96% | 40W Unframed 2J a-Si Module
First Solar, LLC | 38 | 40 | 95% | 40W Thin-Film CdTe Laminate
First Solar, LLC | 38 | 40 | 95% | 40W Thin-Film CdTe Module w/ D-channel mounting rails
United Solar Systems Corp. | 36.9 | 39 | 94.62% | 39W Framed Triple-Junction a-Si Module
Shell Solar Industries | 35.3 | 40 | 88.25% | 40W 12V PowerMax Module
Baoding Yingli New Energy | 35.1 | 40 | 87.75% | 40W Crystalline Silicon Solar Cells
Kyocera Solar, Inc. | 34.8 | 39 | 89.23% | 39W Multicrystal PV Module, Deep Blue, Meridian Frame
Kyocera Solar, Inc. | 34.8 | 39 | 89.23% | 39W Multicrystal PV Module, Deep Blue, Samurai Frame
Isofoton | 32.2 | 36 | 89.44% | 36W Monocrystalline Rail Mounted Module
Shell Solar Industries | 31.7 | 38 | 83.42% | 36W 12V PowerMax Module
United Solar Systems Corp. | 30.3 | 32 | 94.69% | 32W Framed Triple-Junction a-Si Module
United Solar Systems Corp. | 29.3 | 31 | 94.52% | 31W Field Applied 3J a-Si Laminate
Dunasolar Inc. | 28.8 | 30 | 96% | 30W Unframed 2J a-Si Module
Energy Photovoltaics, Inc. | 28.8 | 30 | 96% | 30W Unframed 2J a-Si Module
United Solar Systems Corp. | 27.5 | 29 | 94.83% | 29W Field Applied 3J a-Si Laminate, Purlin-Mounted
United Solar Systems Corp. | 26.9 | 29 | 92.76% | 29W Field Applied 3J a-Si Laminate, Deck-Mounted
Evergreen Solar | 26.7 | 30 | 89% | 30W String Ribbon poly-Si Module
AstroPower, Inc. | 26.5 | 30 | 88.33% | 30W Single Crystal Module w/o connectors (was AP-30)
AstroPower, Inc. | 26.5 | 30 | 88.33% | 30W Single Crystal Module w/o connectors (was AP-30) B
GE Energy | 26.5 | 30 | 88.33% | 30W Single Crystal Module w/o connectors
GE Energy | 26.5 | 30 | 88.33% | 30W Single Crystal Module w/o connectors B
Baoding Yingli New Energy | 26.3 | 30 | 87.67% | 30W Crystalline Silicon Solar Cells
Evergreen Solar | 24.9 | 28 | 88.93% | 28W String Ribbon poly-Si Module
Evergreen Solar | 22.2 | 25 | 88.8% | 25W String Ribbon poly-Si Module
United Solar Systems Corp. | 15.7 | 17 | 92.35% | 17W Shingle 3J a-Si Module
United Solar Systems Corp. | 13.9 | 15 | 92.67% | 15W Shingle 3J a-Si Module
Atlantis Energy, Inc. | 11.4 | 13.3 | 85.71% | 13.3W Shingle Module (Sharp cells)
Atlantis Energy, Inc. | 11 | 12.2 | 90.16% | 12.2W Shingle Module (Siemens cells)
Atlantis Energy, Inc. | 11 | 12.2 | 90.16% | 12.2W Shingle Module (Astropower cells)
Atlantis Energy, Inc. | 10.9 | 12.7 | 85.83% | 12.7W Shingle Module (Sharp cells)
Atlantis Energy, Inc. | 10.8 | 12 | 90% | 12.0W Shingle Module (Astropower cells)
Atlantis Energy, Inc. | 10.7 | 11.8 | 90.68% | 11.8W Shingle Module (Astropower cells)
Atlantis Energy, Inc. | 10.5 | 11.6 | 90.52% | 11.6W Shingle Module (Solarex cells)
Atlantis Energy, Inc. | 10.2 | 11.9 | 85.71% | 11.9W Shingle Module (Sharp cells)
Atlantis Energy, Inc. | 9.9 | 11 | 90% | 11.0W Shingle Module (Solarex cells)